## Slide 1: Investigating the Potential of Machine Learning in Alarm Management
18. October 2024
Elena Kranz

## Slide 2
We acknowledge the Traditional Owners of country throughout Australia and recognise their continuing connection to land, waters and culture.
We pay respect to Elders past, present and emerging.

## Slide 3: Agenda - Alarm Management POC
  Why: Problem Statement
  How: Project Roadmap
    Value Proposition: Data Acquisition
    Value Proposition: Exploratory Data Analysis
    + Traditional Machine Learning Clustering
  Next steps: Deep Learning for Clustering and Classification
  Q&A

## Slide 4: I. Problem Statement: High Volume of Alarms
xkcd 1106
Challenges:
High Volume and Increased Complexity of Alarms
Lack of Alarm Interpretation and Contextualization
Poor Display and Usability
Sometimes it’s up to 6500 alarms per minute
Operator

## Slide 5: I. Problem Statement: High Volume of Alarms
Vision: automation with machine learning
Sense Making
Consolidating alarms
Decision Making
Identify incident
Action Taking
Tie alarms into process
Validate with NSP
Feedback
Clustering
+ Chat Bot for better Information Integration
Classification
Proposing process
Current state: overwhelming, manual, time consuming process
Current Process

## Slide 6: II. Project Roadmap
Data Acquisition
Consolidating multiple data sources in DB
Building data pipelines
Exploratory Data Analysis
Filtering
Next Steps
Increase model complexity
Feedback Loop with Control Room
Cleaning, Parsing
Mapping
Developing interface
Apply Traditional Clustering
Find pattern and relationships
Validation of alarm cluster
Validation of Mappings
Test on real time data
Incorporate subject matter expertise
Refine models over time
Recommend actions

## Slide 7: Data Acquisition
We want to connect multiple data sources across AEMO to enrich the alarms with valuable information
We already consolidated the following datasets in a PostgreSQL DB:
  Archive Alarms Files
  Incident Reports of Non-Credible Contingency Events
  Planned and Unplanned Outages
  Grid Connectivity
  Control Room Logs
  Market Notices
cleaning, parsing
develop interface, building data pipelines

## Slide 8: Mapping Challenge: System Integration and Data Consistency Issues
Inconsistent identifiers between systems lead to challenges in linking relevant data across platforms.
Machine learning could be useful to handle these inconsistencies
eid | type | equipment_id | alarm_equipment_id | outage_id | Control Room Log
204426 | LINE/LN | STATE.SUBREGION.SUBSTATION.330.LNXX | LN.XX.0 | ND. SUBSTATION.330.LNXX | The Sub A to Sub B line tripped and failed to auto reclose. 5412 breaker also opened at A. MN108414 and MN 108415 was published. N_LDTM_XX-OPEN was invoked from 1445 hrs. NOS entry was submitted (TG_771784).
2536365 | BKR/BK/CB | STATE.SUBREGION. SUBSTATION.ISOL.5411 | SUBSTATION.ISOL.5411.ISOL | CB. SUBSTATION.BREAKR.5411 | 
3924033 | Transformer/TX/XFMR | STATE.SUBREGION. SUBSTATION.1A.1AH | SUBSTATION.XF.1AH | XFMR. SUBSTATION.1A | 

## Slide 9: II. Project Roadmap
Data Acquisition
Consolidating multiple data sources in DB
Building data pipelines
Exploratory Data Analysis
Filtering
Next Steps
Increase model complexity
Feedback Loop with Control Room
Cleaning, Parsing
Mapping
Developing interface
Apply Traditional Clustering
Find pattern and relationships
Validation of alarm cluster
Validation of Mappings
Test on real time data
Incorporate subject matter expertise
Refine models over time
Recommend actions
Dashboard

## Slide 10: EDA - Analyse Alarm Flooding Events
Spike as Indicator?
Power System Event
Control Room Logs
Outages
Outages
Already filtered down from 6500 alarms per minute
Alarm Count
Timestamp

## Slide 11
EDA - Analyse Alarm Flooding
Indicates a loss of SCADA points

## Slide 12: EDA - Analyze Alarm Flooding
We can apply filters:
  We can filter out a list of attributes approved by Operators
  Equipment related alarms are most important to identify power system events
Now we have less noisy data as machine learning input
Alarm Count doesn’t indicate mayor power system events

## Slide 13: Cluster Alarms from a non-credible contingency event
1. Alarms which are physically related
2. Filter noise
Trip of Sub A – Sub B 330 kV line and Sub A 330/33 kV transformer
Filter options:

## Slide 14: Cluster Alarms from a non-credible contingency event
Choose cluster algorithm
Alarm Cluster plotted in 2D Embedding Space
Cluster
Cluster 0

## Slide 15: Cluster Alarms from a non-credible contingency event

## Slide 16: How does this help the Control Room again?
You can imagine there is a lot of different system conditions
We will use a Combination of Machine Learning and Traditional Coding
NSW Substation A to Substation B line X and transformer 1A deenergized |  | 
Sense Making | Decision Making | Action Making
The Substation A – Substation B 330 kV line and 1A transformer tripped. + precise sequence of equipment faults Additional information: it could be related to a planned outage – NSP is testing cable,… Feature to zoom into details |  | Suggesting actions that can be taken: Constraint invocation Inform market of incident Resecure the system and improve the situation (reserve, system strength, etc)

## Slide 17: II. Project Roadmap
Data Acquisition
Consolidating multiple data sources in DB
Building data pipelines
Exploratory Data Analysis
Filtering
Next Steps
Increase model complexity
Feedback Loop with Control Room
Cleaning, Parsing
Mapping
Developing interface
Apply Traditional Clustering
Find pattern and relationships
Validation of alarm cluster
Validation of Mappings
Test on real time data
Incorporate subject matter expertise
Refine models over time
Recommend actions

## Slide 18: Idea Model Input: Graph based on Topology + additional Logging Sources
Alarm Type
Planned Outage
Constraints
Weather events
+ dynamic topology changes

## Slide 19: Training a Variational Graph Autoencoder
snapshots of the grid as time series of SCADA scans
New Alarm sequence
Clusters Alarms for critical event

## Slide 20
Thank you for your attention.
xkcd 1794

## Slide 21: POV Control Room
Consolidate related alarms
Check SLD/Wallboard
Coordination with TNSP’s
Look up Planned Outages
Weigh up information from different EMS Applications
Weather and Environmental Considerations
Look up historical Logs and outages under similar conditions
System Security Assessment
….
Administrative Streamlining:
Log “subjective” investigations
Create templates for reporting and actions
…

## Slide 22: Traditional Clustering - Conclusion
Requires manual filtering steps on the topology and the time window beforehand
Hyperparameter tuning can be very individual to each case
Clusters are based only on the Euclidean distance of the alarm embeddings
Useful for investigating past power system events by mapping different logging sources and clustering the alarms
Useful benchmark for comparison with more advanced models
And to label alarm cluster of relevant power system events for further machine learning model improvements
For now, focus on unsupervised learning

## Slide 23: Which model should we use next?
IEEE Xplore Full-Text PDF:
Integrate time and connectivity pattern?

## Slide 24: EDA - Derivative of exception_name Alarm Count per Minute
Indicates a loss of SCADA points

## Slide 25: I. What is an Alarm?
Modelling Information
Alarm clients can be on any computer (equipment or application) within the site.
Attributes
Bilder von assets

## Slide 26
EMS_ID
EID
NOS_ID
SCADAMOM
client_composite_id
Inconsistent ids between systems
Mapping attempts across AEMO
cim_mrid
EMS Alarms
obj_mrid
STPASA database Constraints maps to DUID
NEMMCO oracle database
EPSOC_Log
Market notice
NETMOMID
OPDMS Mapping
ODS Mapping
Weather, Generation, Load Forecast
MIAMI

## Slide 27: EDA - Spike originated from the share of XMMS category in the Alarm Count per Minute
80%
100%
60%
40%
20%
0%